TABLES

Table 1: Main parameters of the system

| Parameter | Value |
| --- | --- |
| Fuel cell efficiency (FC) | app. 60 % |
| Electrolyser efficiency (EL) | app. 70 % |
| Hydrogen storage pressure maximum (pmax) | 50 bar |
| Battery charging efficiency (C) | 95 % |
| Battery discharging efficiency (D) | 95 % |
| Heat pump coeff. of performance (CoPHP) | 3.0 |

Table 2: Cost of the supply from the public electric grid (Germany)

| Energy and supply costs (EUR/kWh) | Network costs (EUR/kWh) | Taxes, fees, levies and charges (EUR/kWh) | Total price (EUR/kWh) |
| --- | --- | --- | --- |
| 0.1640 | 0.0909 | 0.1064 | 0.3613 |

Table 3: System parameters and results of experiments 1…9

| System structure |  | Experiment |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| FC-HP thermal integration | No/Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes |
| Battery | No/Yes | No | No | Yes | No | Yes | Yes | Yes | No | No |
| Technic parameters |  |  |  |  |  |  |  |  |  |  |
| PV size | m2 | 147.7 | 149.3 | 108.1 | 129.9 | 109.2 | 111.2 | 98.4 | 128 | 128.7 |
| Hydrogen storage tank capacity | kWh | 6914.8 | 6926.1 | 6632.3 | 6157.2 | 6058.2 | 5945.8 | 5717.0 | 6190.6 | 6147.2 |
|  | kg | 175.5 | 175.8 | 168.4 | 156.3 | 153.8 | 150.9 | 145.1 | 157.2 | 156.1 |
| Electrolyser max. power | kW | 13 | 13 | 13 | 13 | 13 | 11 | 10 | 14 | 13 |
| Electrolyser min. power | % of max P | 0 % | 10 % |  |  |  |  |  |  |  |
| Electrolyser efficiency | % | See Figure 8 (10 years) |  |  |  |  |  |  |  |  |
| Fuel cell max. power | kW | 13 | 13 | 13 | 13 | 13 | 10 | 10 | 12 | 12 |
| Fuel cell efficiency | % | See Figure 10 (10 years) |  |  |  |  |  |  |  |  |
| Battery required capacity | kWh | 0 |  | 16 | 0 | 7 | 6 | 20 | 0 |  |
| Battery nominal capacity | kWh | 0 |  | 26.7 | 0 | 11.7 | 10 | 33.3 | 0 |  |
| Batt. max. charging power | kW | 0 |  | 8 | 0 | 8 | 8 | 8 | 0 |  |
| Batt. max. discharg. power | kW | 0 |  | 8 | 0 | 8 | 8 | 8 | 0 |  |
| Battery charging efficiency | % | n.a. |  | 95% | n.a. | 95% |  |  | n.a. |  |
| Battery discharging effic. | % | n.a. |  | 95% | n.a. | 95% |  |  | n.a. |  |
| Economic parameters |  |  |  |  |  |  |  |  |  |  |
| PV power plant CAPEX | EUR/m2 | 210 |  |  |  |  |  |  |  |  |
| Electrolyser CAPEX + OPEX | EUR/kW | 800+480 |  |  |  |  |  |  |  |  |
| Fuel cell CAPEX + OPEX | EUR/kW | 800+480 |  |  |  |  |  |  |  |  |
| H2 storage tank CAPEX | EUR/kg | 250 |  |  |  |  |  |  |  |  |
| Battery CAPEX + OPEX | EUR/kWh | 400+400 |  |  |  |  |  |  |  |  |
| Results: operating time |  |  |  |  |  |  |  |  |  |  |
| Electrolyser total | h | 3473.5 | 2932 | 1757.5 | 2826 | 2044 | 2080.5 | 1649.5 | 2763.5 | 2812.5 |
| Electrolyser effective | h | 1661.4 | 1652.3 | 893.5 | 1444.9 | 1014.6 | 1144.2 | 973.4 | 1319.9 | 1428.3 |
| Fuel cell total | h | 5286 | 5280 | 2253.5 | 5314 | 3123.5 | 3447.5 | 2135.5 | 5331.5 | 5326.5 |
| Electrolyser effective | h | 499.4 | 498.7 | 288.3 | 429.5 | 319 | 447.9 | 312.2 | 467.8 | 467.5 |
| Results: energy balance |  |  |  |  |  |  |  |  |  |  |
| PV generated energy | kWh | 27835.3 | 28136.8 | 20372.3 | 24480.7 | 20579.6 | 20956.6 | 18544.3 | 24122.7 | 24254.6 |
| Consumed energy | kWh | 12022.2 | 12022.2 | 12022.2 | 10747.3 | 11152 | 11156.9 | 11415.5 | 10777.4 | 10778.3 |
| Energy supplied to the grid | kWh | 707.4 | 1118 | 152.3 | 534 | 179.8 | 278.8 | 166.3 | 481.1 | 517.9 |
| Energy taken from the grid | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Electrolyser losses | kWh | 8030.1 | 7928.9 | 4132.3 | 6817.9 | 4680.5 | 5004.7 | 3571.8 | 6618.8 | 6730 |
| Fuel cell losses | kWh | 7069.3 | 7058.9 | 3724.5 | 6377.9 | 4353.9 | 4329.6 | 3035.2 | 6227.7 | 6223 |
| Battery charging losses | kWh | 0 | 0 | 168.8 | 0 | 104.5 | 93.5 | 179.1 | 0 | 0 |
| Battery discharging losses | kWh | 0 | 0 | 160.3 | 0 | 99.3 | 88.8 | 170.1 | 0 | 0 |
| Hydrogen produced | kg | 344.5 | 344 | 190 | 303.8 | 216 | 220.1 | 156.4 | 301.1 | 300.5 |
| Results: price of electric energy (by components and total) |  |  |  |  |  |  |  |  |  |  |
| EPPV | EUR/MWh | 129 | 130.4 | 94.4 | 126.9 | 102.8 | 104.7 | 90.5 | 124.7 | 125.4 |
| EPH2_STOR | EUR/MWh | 182.5 | 182.8 | 175.1 | 181.8 | 172.4 | 169.1 | 158.9 | 182.3 | 181 |
| EPEL | EUR/MWh | 69.2 | 69.2 | 69.2 | 77.4 | 74.6 | 63.1 | 56.1 | 83.1 | 77.2 |
| EPFC | EUR/MWh | 69.2 | 69.2 | 69.2 | 77.4 | 74.6 | 57.4 | 56.1 | 71.3 | 71.3 |
| EPBATT | EUR/MWh | 0 | 0 | 88.7 | 0 | 41.8 | 35.9 | 116.8 | 0 | 0 |
| EPTOT | EUR/MWh | 449.9 | 451.6 | 496.6 | 463.5 | 466.3 | 430.1 | 478.4 | 461.4 | 454.8 |
| Results: Annual cost of local supply |  |  |  |  |  |  |  |  |  |  |
| Consumed el. energy | kWh | 12022.2 | 12022.2 | 12022.2 | 10747.3 | 11152 | 11156.9 | 11415.5 | 10777.4 | 10778.3 |
| Final price | EUR/MWh | 449.9 | 451.6 | 496.6 | 463.5 | 466.3 | 430.1 | 478.4 | 461.4 | 454.8 |
| Total cost | EUR | 5409.2 | 5429.6 | 5970.4 | 4981.9 | 5199.8 | 4798.4 | 5460.8 | 4972.5 | 4902.1 |
| Results: Annual cost of traditional supply (from public electric grid) |  |  |  |  |  |  |  |  |  |  |
| Consumed el. energy | kWh | 12014 |  |  |  |  |  |  |  |  |
| Final price | EUR/MWh | 361.3 |  |  |  |  |  |  |  |  |
| Total cost | EUR | 4340.7 |  |  |  |  |  |  |  |  |

Table 4: System parameters and results of experiments 10…18

| System structure |  | Experiment |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 |
| FC-HP thermal integration | No/Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |
| Battery | No/Yes | No | No | No | No | No | No | No | Yes | Yes |
| Technic parameters |  |  |  |  |  |  |  |  |  |  |
| PV size | m2 | 130.4 | 133.7 | 139 | 148.1 | 163.2 | 190 | 172.6 | 132.6 | 132.6 |
| Hydrogen storage tank capacity | kWh | 6083.2 | 5990.6 | 5835.7 | 5619.6 | 5335.5 | 4981.8 | 5128.8 | 5327.8 | 5327.8 |
|  | kg | 154.4 | 152.1 | 148.2 | 142.7 | 135.5 | 126.5 | 130.2 | 135.3 | 135.3 |
| Electrolyser max. power | kW | 12 | 11 | 10 | 9 | 8 | 7 | 7 | 7 | 7 |
| Electrolyser min. power | % of max P | 10 % |  |  |  |  |  |  |  |  |
| Electrolyser efficiency | % | See Figure 8 (10 years) |  |  |  |  |  |  |  |  |
| Fuel cell max. power | kW | 12 | 12 | 12 | 12 | 12 | 12 | 6.2 | 6.2 | 6.2 |
| Fuel cell efficiency | % | See Figure 10 (10 years) |  |  |  |  |  |  |  |  |
| Battery required capacity | kWh | 0 |  |  |  |  |  |  | 6 | 6 |
| Battery nominal capacity | kWh | 0 |  |  |  |  |  |  | 10 | 10 |
| Batt. max. charging power | kW | 0 |  |  |  |  |  |  | 8 | 8 |
| Batt. max. discharg. power | kW | 0 |  |  |  |  |  |  | 8 | 8 |
| Battery charging efficiency | % | n.a. |  |  |  |  |  |  | 95 % |  |
| Battery discharging effic. | % | n.a. |  |  |  |  |  |  | 95 % |  |
| Economic parameters |  |  |  |  |  |  |  |  |  |  |
| PV power plant CAPEX | EUR/m2 | 210 |  |  |  |  |  |  |  |  |
| Electrolyser CAPEX + OPEX | EUR/kW | 800+480 |  |  |  |  |  |  |  | 400+240 |
| Fuel cell CAPEX + OPEX | EUR/kW | 800+480 |  |  |  |  |  |  |  | 400+240 |
| H2 storage tank CAPEX | EUR/kg | 250 |  |  |  |  |  |  |  | 125 |
| Battery CAPEX + OPEX | EUR/kWh | 400+400 |  |  |  |  |  |  |  | 200+200 |
| Results: operating time |  |  |  |  |  |  |  |  |  |  |
| Electrolyser total | h | 2870 | 2933 | 3115 | 3000.5 | 3232.5 | 3404.5 | 3325.5 | 2455 | 2455 |
| Electrolyser effective | h | 1555.0 | 1703.6 | 1875.9 | 2080.9 | 2327.1 | 2627.4 | 2511.2 | 1905.1 | 1905.1 |
| Fuel cell total | h | 5314 | 5299 | 5273.5 | 5233 | 5174.5 | 5085 | 5141.5 | 3230 | 3230 |
| Electrolyser effective | h | 466.6 | 465.1 | 462.9 | 459.2 | 453.8 | 445.7 | 886.5 | 675.9 | 675.9 |
| Results: energy balance |  |  |  |  |  |  |  |  |  |  |
| PV generated energy | kWh | 24575 | 25196.9 | 26195.7 | 27910.7 | 30756.4 | 35807.1 | 32527.9 | 24989.6 | 24989.6 |
| Consumed energy | kWh | 10780.7 | 10784.2 | 10790.4 | 10800.1 | 10814.2 | 10835.4 | 10961.3 | 11221.9 | 11221.9 |
| Energy supplied to the grid | kWh | 733.5 | 1253.6 | 2201 | 3893.5 | 6770.9 | 11927.9 | 9484.9 | 4436.2 | 4436.2 |
| Energy taken from the grid | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| Electrolyser losses | kWh | 6844.9 | 6954 | 7037 | 7097.8 | 7125.1 | 7102.4 | 6770.1 | 5140 | 5140 |
| Fuel cell losses | kWh | 6211.2 | 6193.5 | 6162.6 | 6114 | 6043.6 | 5937.3 | 5307.6 | 4004.1 | 4004.1 |
| Battery charging losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5 | 95.5 |
| Battery discharging losses | kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.7 | 90.7 |
| Hydrogen produced | kg | 300 | 299.2 | 297.6 | 295.3 | 291.7 | 286.6 | 274.4 | 208.1 | 208.1 |
| Results: price of electric energy (by components and total) |  |  |  |  |  |  |  |  |  |  |
| EPPV | EUR/MWh | 127 | 130.2 | 135.3 | 144 | 158.5 | 184.1 | 165.3 | 124.1 | 124.1 |
| EPH2_STOR | EUR/MWh | 179.1 | 176.3 | 171.6 | 165.1 | 156.6 | 145.9 | 148.5 | 150.7 | 75.3 |
| EPEL | EUR/MWh | 71.2 | 65.3 | 59.3 | 53.3 | 47.3 | 41.3 | 40.9 | 39.9 | 20 |
| EPFC | EUR/MWh | 71.2 | 71.2 | 71.2 | 71.1 | 71 | 70.9 | 36.2 | 35.4 | 17.7 |
| EPBATT | EUR/MWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.6 | 17.8 |
| EPTOT | EUR/MWh | 448.5 | 443 | 437.4 | 433.6 | 433.4 | 442.2 | 390.9 | 385.7 | 254.9 |
| Results: Annual cost of local supply |  |  |  |  |  |  |  |  |  |  |
| Consumed el. energy | kWh | 10780.7 | 10784.2 | 10790.4 | 10800.1 | 10814.2 | 10835.4 | 10961.3 | 11221.9 | 11221.9 |
| Final price | EUR/MWh | 448.5 | 443 | 437.4 | 433.6 | 433.4 | 442.2 | 390.9 | 385.7 | 254.9 |
| Total cost | EUR | 4835.6 | 4776.9 | 4719.4 | 4682.4 | 4686.8 | 4791.9 | 4284.7 | 4327.8 | 2860.1 |
| Results: Annual cost of traditional supply (from public electric grid) |  |  |  |  |  |  |  |  |  |  |
| Consumed el. energy | kWh | 12014 |  |  |  |  |  |  |  |  |
| Final price | EUR/MWh | 361.3 |  |  |  |  |  |  |  |  |
| Total cost | EUR | 4340.7 |  |  |  |  |  |  |  |  |

Table 5: Annual electricity supply cost sensitivity to key CAPEX variations

| Component | CAPEX variation | Annual electricity supply cost variation |
| --- | --- | --- |
| PV power plant | ± 20 % | ± 7.3 % |
| Electrolyser | ± 20 % | ± 1.5 % |
| Fuel cell | ± 20 % | ± 1.3 % |
| Hydrogen storage | ± 20 % | ± 8.9 % |
| Battery | ± 20 % | ± 1.0 % |